December 24th, 2013

Via Electronic Mail

Ms. Brenda Edwards

U.S. Department of Energy

Building Technologies Program, Mailstop EE-2J

1000 Independence Ave., SW

Washington, DC  20585-0121

Re: Docket Number EERE-2010-BT-STD-0011; RIN 1904-AC22

The following comments are submitted for the record of the Department’s above-captioned rulemaking regarding the Furnace Fan Standards Notice of Proposed Rule. They are submitted on behalf of the Northwest Energy Efficiency Alliance and the Northwest Power and Conservation Council.

The Northwest Energy Efficiency Alliance is a non-profit organization working to encourage the development and adoption of energy-efficient products and services. NEEA is supported by the region’s electric utilities, public benefits administrators, state governments, public interest groups and efficiency industry representatives. This unique partnership has helped make the Northwest region a national leader in energy efficiency.

The Northwest Power and Conservation Council (Council) is an interstate compact between the states of Idaho, Montana, Oregon and Washington authorized by the Northwest Electric Power Planning and Conservation Act of 1980 (PL96-501).  The Council’s role is to ensure that the Northwest’s electric power system will provide adequate and reliable energy at the lowest economic and environmental cost to its citizens.  The Congress charged the Council with developing integrated electric power plans for the Northwest. These plans are to rely on cost-effective conservation as their first priority resource.

Overview

We strongly support the proposed standard levels in the Notice of Proposed Rule, as those levels are described in terms of requiring brushless permanent magnet (BPM) fan motors, with furnace staging, as the minimum technology level needed to meet the standards. However, we are not yet convinced that the proposed standard levels in FER terms are set properly to ensure that most furnace fans that are so equipped will actually meet the standards when tested.

Of course, such assurance isn’t possible until the Final Rule for the Test Procedure is published, and manufacturers have had the time and opportunity to test their furnace fans models that are so equipped to verify whether or not the resulting FER ratings would allow them to meet the proposed standards. We heard from more than one manufacturer at the December 3rd public meeting that they had recommended proposed test procedure changes that would materially alter the FER ratings of their products, and that using the test procedure as currently proposed would result in some of their most efficient products failing to meet the proposed standards. Clearly there is a need for product testing using the final test procedure, and a re-assessment of the derivation of the proposed FER equations and standard levels. We don’t believe the Department can make an informed decision with regard to the proposed standards and the equations used to derive minimum FER ratings until these steps have been taken.

We do believe, however, that the life cycle cost and energy savings analyses are robust enough at this time to make it clear that the technologies upon which the proposed standards are based are the right ones – ones that deliver positive life cycle cost outcomes for the vast majority of furnace fan purchasers, with no adverse impact on product utility, and with significant energy savings for consumers and the nation as a whole. While a higher standard than TSL4 is certainly technologically feasible, the results of DOE’s analyses suggest to us that the higher levels would be difficult to economically justify at this time.

The Department’s methodology for constructing fan efficiency curves for baseline and higher efficiency models has so far depended substantially on the use of what DOE refers to in Chapter 5 of the TSD as “performance information from publicly-available product literature.” Unfortunately, because the test procedure has not been finalized, the relationship between certification testing and manufacturer product literature performance data, upon which DOE has depended, has not yet been established. In other rulemakings (such as the fluorescent lamp and fluorescent lamp ballast rulemakings), the differences between tested performance values and catalog performance values has been disconcertingly large. We strongly suggest that it is imperative to use as much actual product test data as possible, derived from the final test procedure, when establishing the standards to which manufacturers will have to certify their products.

The most important step that DOE can take right now in order to publish an appropriate Final Rule for this rulemaking in the spring of 2014 is to allow enough time between the publishing of the Final Rule for the Furnace Fan Test Procedure and the Department’s consideration of the Proposed Rule for Standards – enough time for the manufacturers to submit product test data to DOE. We do not support a decision on standards before there is sufficient data with which to verify that the proposed FER values will not disqualify from compliance the majority of the very products upon which they are founded, and for which DOE’s economic analyses are valid. While we understand DOE’s intent to meet its rulemaking schedule for these products, we believe it is more important to take the time to get it right.

Final Issues

Effective Date of Standards

If the Department ultimately proposes standards that are based on constant-torque BPM motors and furnace staging, there is no reason to require an effective date more than 3 years from the Final Rule date.

The technology required to meet the TSL4 standards is well known and widely used, and requires little more than expansion of current production capacity for these models, which mostly means buying different furnace fan motors and the associated controls. Three years of lead time should be sufficient to allow a ramping up of motor manufacturing capacity and a gradual shift of air handler manufacturing lines to incorporate them. With market share of these products at a third of shipments before 2020, the changes should be minimally disruptive. And the Department clearly has the legal discretion to choose the earlier effective date.

Scope

We continue to be disappointed that DOE is choosing to cover only two-thirds of furnace fan products.

The statutory language requiring the Department to conduct a rulemaking for efficiency standards for these products is quite clear – DOE is directed to “consider and prescribe energy conservation standards or energy use standards for electricity used for purposes of circulating air through duct work.” Clearly such products include the indoor blower/cool units used with split system heat pump and air conditioning systems, which meet this definition when installed without an outdoor unit. And clearly residential hydronic air handlers of any kind meet this definition, as well.

We recognize that additional specifications would have to be made to the furnace fan test procedure to allow the regulation of these products, but we also recognize that leaving out such a large fraction of the technical furnace fan market will leave substantial energy savings unaddressed.

Fan Efficiency Rating (FER)

Use of a Single Weighted-Average FER

We understand the Department’s choice of a single FER rating point, using average operating hour assumptions for the three furnace fan modes (heating, cooling and constant circulation) for describing furnace fan efficiency, but we strongly urge the Department to require the reporting of certified values for FERheat, FERmax and FERcirc.

Just as in the case of residential heat pump systems, DOE’s choice of test procedure and rating metrics means that the field efficiency of these systems depends strongly on the climate in which they’re operated, which substantially determines the operating hours in each operating mode. DOE describes the efficiency of a heat pump system using what is commonly described as the HSPF. However, this rating is technically the Region IV HSPF, and there are HSPF ratings that can be calculated for the other AHRI climate regions. In fact, many manufacturers publish the Region V HSPF ratings for their systems, which is the rating that Pacific Northwest utilities often use to estimate annual energy use for these systems. It is important to be able to do the same for furnace fans, using the appropriate climate zone bin weightings and modal operating hours for these products.

NEEA has the field data with which to determine annual modal operating hours for furnace fans, in a statistically significant number of homes, in the Pacific Northwest region. We will do our best to provide this data to DOE before a decision must be made on the proposed furnace fan standards, but we are unable to meet the December 24th, 2013 deadline for comments with this data. The data will no doubt show the Department that different FER values than those proposed in the test procedure would result if Pacific Northwest data were used to specify modal operating hours.

While we are not suggesting that DOE propose regional standards at this point, we strongly urge the Department to make it possible for annual energy use values that are reasonably representative of a typical annual use cycle in our region to be derived from the outputs of the furnace fan test procedure.

Modal Operating Hours

The Department’s assumptions about the use of constant circulation mode are tenuous at best. DOE says that it referred to a 2010 Minnesota survey and a 2003 Wisconsin study. Then the Department discounts the data because it believes they are not representative of consumer practices for the U.S. as a whole. In these northern States, many homes have low air infiltration, and there is a high awareness of indoor air quality issues, which could lead to significant use of constant circulation.” Then DOE derived “appropriate assumptions for other regions” by using “information from manufacturer product literature (which suggests very little use in humid climates) and consideration of climate conditions in other regions.” The Department has in no way demonstrated the degree to which the use of constant circulation mode is related to climate, and in fact, a more recent study referred to in the December 3rd public meeting suggests that at least some constant circulation mode is used in as many as 19 percent of homes. The Department’s sensitivity analysis looked only at constant circulation mode use that is less than the assumed 11 percent of furnace fan-equipped households.

NEEA will attempt to timely provide some field data that would add to the very small amount of data currently available, but in the meantime, we believe that DOE’s estimate of 400 hours per year may be overly conservative, and that the savings associated with BPM-equipped fans may therefore be somewhat larger than estimated at this time. We disagree with stakeholders who suggest that 400 hours per year is too high.

BPM Motor Lifetime and Repair Frequency

As in the case of constant circulation mode hours, we believe the Department has insufficient data to properly estimate the frequency and nature of BPM motor repair. Manufacturers stated at the December 3rd public meeting that they have warranty data, but warranty data reflects repair or replacement frequency only during the warranty period, which is typically a small fraction of a furnace fan lifetime. The anecdotal information we have received from a small number of HVAC contractors suggests that BPM motors did at one time experience more frequent failures and higher repair incidence, but that in recent years this has been much less true.

We will attempt to acquire some field survey data in a timely fashion to submit to this docket, but for now, we believe that DOE’s current assumptions may unfairly penalize BPM motors in the life cycle cost analysis.

Summary

The Department has brought this rulemaking a long way toward a highly appropriate set of standards for these important and ubiquitous products. The potential energy savings are significant.

We very much support DOE’s analytical work in establishing the technology basis for the proposed standard levels – constant-torque BPM motor-driven fans with system staging. This level of technology is substantially more efficiency than the baseline technology, is cost-effective in all of the product classes for which standards are being set, and with no loss of product utility or non-energy-related performance.

We thank the Department for providing the extensive space for comment in this docket, and for carefully considering all of the input and counsel from stakeholders along the way. We believe we’re on the verge of a very good rule.

Charlie Stephens
Senior Energy Codes and Standards Engineer

NORTHWEST ENERGY EFFICIENCY ALLIANCE

421 SW Sixth Avenue, Suite 600, Portland, Oregon 97204

Tom Eckman

Manager, Conservation Resources

Northwest Power & Conservation Council

# Footnotes

16 United States Code Chapter 12H (1994 & Supp. I 1995). Act of Dec. 5, 1980, 94 Stat. 2697. Public Law No. 96-501, S. 885.

Northwest Power Act, §4(e)(1), 94 Stat. 2705.

Ingersoll Rand said their top-of-the-line products won’t likely meet the proposed standards, and Rheem, Lennox and Goodman all stated that only their constant flow BPM products with staging (the basis for TSL5) would appear to meet the proposed standards.

42 U.S.C. 6295(f)(4)(D), FR 78 No.207, October 25, 2013, at 64074(1)

When installed with an outdoor unit, these products become part of a heat pump or central air conditioning system, with their own test procedure and efficiency metrics. But they are frequently installed without an outdoor unit, and in such installations, they are furnace fans, generally used as electric forced air furnaces, or as the air handler for a gas-fired hydronic heating system; cooling may or may not be supplied using the air handler refrigerant coil.

At a minimum, these products would have to be tested at the higher external static pressure levels currently proposed for the Test Procedure, there would have to be some specification of what fan/coil combinations (basic models) would be tested, and there would have to be direct measurement of fan air flow for these particular product classes.

78 FR No.207, Friday, October 25, 2013. p.64094(2).

Ibid.