## Slide 1
DOE Residential Furnace Standard Development
LCC and Impact Analysis
Yanda Zhang
March 7 2015

## Slide 2: Products – Tech Level
Trial Standard Levels (TSL) based on efficiency levels in the table
Efficiency Level | AFUE % | Technology |  | Efficiency Level | AFUE % | Technology
0-Baseline | 80 | - |  | 0-Baseline | 80 | -
1 | 90 | Baseline + condensing secondary heat exchanger |  |  |  | 
2 | 92 | Level 1 + Increased secondary heat exchanger area |  | 1 | 92 | Baseline + condensing secondary heat exchanger
3 | 95 | Level 2 + Increased secondary heat exchanger area |  | 2 | 95 | Level 1 + Increased secondary heat exchanger area
4 Max_tech | 98 | Level 3 + Increased secondary heat exchanger area + Step- modulating combustion + Constant-airflow brushless permanent magnet (BPM) blower motor |  | 3 Max_tech | 98 | Level 2 + Increased secondary heat exchanger area
Non-Weatherized Gas Furnaces (NWGF)
Mobile Home Gas Furnaces
(MHGF)

## Slide 3: Market
CA: 10.52% of national Gas Furnace Shipments
New Owner: product switch/addition, similar to new construction installation
 | NWGF | MHGF
Residential | 97% | 100%
Commercial | 3% | 0%
New Construction | 25% | 50%
Replacement & New Owner | 75% | 50%
Replacement | 67.5% | 50%
New Owner | 7.5% | 0%

## Slide 4: Potential Savings
US Savings: 2.78 quads
  Full-fuel-cycle savings: life cycle source energy savings
  For furnaces purchased in 30-year period (2021–2050)
CA first-year energy savings
  IOU 2015 incentive program natural gas savings goal: 38 Million Therm
 | Million Therm | % of 2015 Goal for IOU Incentive Programs
90% AFUE | 4.5 | 12%
92% AFUE | 6.8 | 18%
95% AFUE | 7.2 | 20%
98% AFUE | 9.5 | 25%

## Slide 5: Monte Carlo Method
Reflect Variability & Uncertainty of furnace usage in buildings
Traditional approach: prototype buildings with fixture energy use and cost information representing typical/average market conditions  Results reflect typical/average outcome
Monte Carlo: random selected buildings and inputs  probability distributions of LCC and PBP  show the fraction of market with LCC > 0
  Perform 10,000 calculations
  Each calculation is independent
Analysis Tool: Excel spreadsheets combined with Crystal Ball

## Slide 6: Residential Furnace LCC Spreadsheet Flow Chart

## Slide 7: Building Sample
RECS 2009: 12,083 homes /1606 in CA
CBECS 2003: 5,215 buildings
Furnace population weights in 2021
  How representative a particular household is of other households in the distribution—either regionally or nation
  The selection of a household was based on its sample weight
Building heating load (BHL):
  RECS and CBEC reported annual heating fuel consumption and AFUE
  Building shell efficiency index adjustment (0.73 ~ 0.97)  better building envelope in 2021
  Historic heating degree days adjustment (0.94 – 1.05)  better reflect historic average climate
  Adjustment factors depend on building type, new construction vs replacement
Furnace location

## Slide 8: CA Building Sample
Part of South region
  DIVISION 10: Pacific Census Division (AK, CA, HI, OR, WA)
  REPORTABLE_DOMAIN: #26
  Weather station ID available for further location identity
Total 1606 samples: 741 (46%) with natural gas for space heating

## Slide 9: CA Building Sample

## Slide 10: Two Major Components of LCC Calculation
Installed Costs
Operating Costs

## Slide 11: Installed Cost – Components
Total Consumer Price
  Product Prices
  Shipping Cost
  Markup
  Future Product Prices (learning curve)
Installation Cost

## Slide 12: Total Consumer Price – Future Product Cost
“learning” or “experience” curve phenomenon
  Real product costs trend downward over time
For furnace: b = 0.937

## Slide 13: Total Consumer Price – Average Prices

## Slide 14: Installed Cost – Installation Cost
Installation Type
  New Construction
  Existing building - Replacement
  Existing building - New owner
Basic installation costs –all new & replacement furnaces
  Include putting in place and setting up the furnace, gas piping, ductwork, electrical hookup for the thermostat, permit, removal or disposal fees, and, when applicable, additional labor hours for an attic installation.
Installations adders
  non-condensing furnaces: these additional costs included updating flue vent connectors, vent resizing, and chimney relining.
  For condensing furnaces, these additional costs included adding a new flue vent (PVC), combustion air vent for direct vent installations (PVC), concealing vent pipes for indoor installations, addressing an orphaned water heater (by updating flue vent connectors, vent resizing, or chimney relining), and condensate removal. Freeze protection (heat tape) is accounted for in the cost of condensate removal for a fraction of NWGFs installed in attics.

## Slide 15: Installation Cost Adders

## Slide 16: Installed Cost – Average Values

## Slide 17: Two Major Components of LCC Calculation
Operating Costs

## Slide 18: Operating Costs – Components
Annual Energy Use Savings
Energy Prices
Repair Cost
Maintenance Cost
Lifetime
Discount Rates

## Slide 19: Operating Costs (1)
Building Heating Load

## Slide 20: Operating Costs (2)

## Slide 21: Operating Costs – Lifetime
Weibull distribution
Same across the different product classes and efficiency levels.

## Slide 22: Operating Costs – Discount Rates
Separate discount rate distributions for six income groups

## Slide 23: Residential Furnace LCC Spreadsheet Flow Chart

## Slide 24: Product Switching
Customer response to potential amended furnace standards
  the furnace that meets a particular standard level
  a heat pump, or
  an electric furnace.
Allow for the possibility of electric water heater installation to avoid expensive re-sizing of the vent system

## Slide 25: LCC Results - Average

## Slide 26: LCC Results - Distribution

## Slide 27: Impact Analysis – Trial Standard Levels (TSLs)

## Slide 28: Next Step
Support TSL 3 (92% AFUE) based new standards
  TSL 3 is cost effective on average
  May not be cost effective for CA  but standard should be based on regional average
Some CA stakeholders oppose setting standards based on condensing technology
  Investigate cost effectiveness in CA
  Low NOx water heater requirements
  Allow CA Title 24 to set standards

## Slide 29
Yanda Zhang
ydzhang@trcsolutions.com