## Sheet1
0.8
|  |  |  | Manual J Design Load |  | Equipment Type | Equipment Sizing
Building Type | Location | Description | Unit Size (ft2) | Heating | Cooling | Furnace/AC, HP | Heating Output (Btu/h) | BTUh Input 80 AFUE | BTUh 80 per sq ft | Cooling (tons) | Notes
SF | Davis, CA | 15% beyond 2013 | 2800 | 30450 | 34550 | Furnace/AC | 60000 | 75000 | 26.7857 | 3.5
SF | El Dorado Hills, CA | Cond Attic, ~30% < 2008 T24 | 3785 |  |  | Furnace/AC | 92000 | 115000 | 30.3831 | 4 | ET project test house
SF | El Dorado Hills, CA | Cond Attic, ~30% < 2008 T24 | 2762 |  |  | Furnace/AC | 92000 | 115000 | 41.6365 | 3.5 | ET project test house
SF | Vacaville, CA | 2008 Title 24 compliant | 2605 |  |  | Furnace/AC | 84000 | 105000 | 40.3071 | 4 | ET project unimproved reference house
SF | Vacaville, CA | 2008 Title 24 compliant | 2368 |  |  | Furnace/AC | 66000 | 82500 | 34.8395 | 4 | ET project unimproved reference house
SF | Davis, CA | 50% beyone 2008, ZNE | 1839 | 27271 | 27408 | CombHyd/AC | 50000 | 62500 | 33.9859 | 3 | Manual J completed by DEG but not used by installing HVAC contractor
SF | Davis, CA | 30-35% beyond 2013 | 1943 | 44450 | 24443 | Furnace/AC | 62800 | 78500 | 40.4014 | 3 | DEG did not complete or review Manual J calcs
SF | Davis, CA | 30-35% beyond 2013 | 2896 | 42730 | 29017 | Furnace/AC | 71800 | 89750 | 30.991 | 3.5 | DEG did not complete or review Manual J calcs
SF | Davis, CA | 30-35% beyond 2013 | 3305 | 51502 | 29902 | Furnace/AC | 89000 | 111250 | 33.6611 | 3.5 | DEG did not complete or review Manual J calcs
SF | Davis, CA | 30-35% beyond 2013 | 3831 | 61618 | 38163 | Furnace/AC | 89000 | 111250 | 29.0394 | 4 | DEG did not complete or review Manual J calcs
SF | Davis, CA | 30-40% beyond 2013 | 1775 | 32906 | 18658 | Furnace/AC | 52800 | 66000 | 37.1831 | 2.5 | DEG did not complete or review Manual J calcs
SF | Davis, CA | 30-40% beyond 2013 | 1833 | 34978 | 19379 | Furnace/AC | 52800 | 66000 | 36.0065 | 2.5 | DEG did not complete or review Manual J calcs
SF | Davis, CA | 30-40% beyond 2013 | 2081 | 38394 | 22826 | Furnace/AC | 52800 | 66000 | 31.7155 | 3 | DEG did not complete or review Manual J calcs
SF | San Jose, CA | 68% beyond 2008, ZNE | 3170 | 16276 | 18846 | Heat Pump | 24000 | 30000 | 9.4637 | 2
SF | San Mateo, CA | 50% beyond 2008 | 3442 | 51710 | 48684 | CombHyd/AC (2 systems) | 86100 | 107625 | 31.2682 | 6.5 | DEG did not complete or review Manual J calcs
SF | Sacamento, CA | 28% beyond 2008 | 1268 | 15741 | 15681 | Heat Pump | 20285 | 25356.25 | 19.997 | 2 | DEG did not complete or review Manual J calcs
MF | Davis, CA | 30-40% beyond 2008 | 1282 | 17196 | 31200 | Heat Pump | 19700 | 24625 | 19.2083 | 3 | EnergyPro load sizing calcs
MF | Davis, CA | 30-40% beyond 2008 | 1080 | 17204 | 30640 | Heat Pump | 19700 | 24625 | 22.8009 | 3 | EnergyPro load sizing calcs
MF | Davis, CA | 30-40% beyond 2008 | 1000 | 15786 | 30245 | Heat Pump | 19700 | 24625 | 24.625 | 3 | EnergyPro load sizing calcs
MF | Davis, CA | 30-40% beyond 2008 | 1282 | 17196 | 33170 | Heat Pump | 19700 | 24625 | 19.2083 | 3 | EnergyPro load sizing calcs
MF | Davis, CA | 30-40% beyond 2008 | 1282 | 15053 | 32806 | Heat Pump | 19700 | 24625 | 19.2083 | 3 | EnergyPro load sizing calcs
MF | Davis, CA | 30-40% beyond 2008 | 1080 | 14660 | 30990 | Heat Pump | 19700 | 24625 | 22.8009 | 3 | EnergyPro load sizing calcs
MF | Davis, CA | 30-40% beyond 2008 | 1000 | 13539 | 30554 | Heat Pump | 19700 | 24625 | 24.625 | 3 | EnergyPro load sizing calcs
MF | Davis, CA | 30-40% beyond 2008 | 1282 | 15053 | 35094 | Heat Pump | 19700 | 24625 | 19.2083 | 3 | EnergyPro load sizing calcs
MF | Davis, CA | 30-40% beyond 2008 | 1282 | 16005 | 33864 | Heat Pump | 19700 | 24625 | 19.2083 | 3 | EnergyPro load sizing calcs
MF | Davis, CA | 30-40% beyond 2008 | 1080 | 15461 | 32243 | Heat Pump | 19700 | 24625 | 22.8009 | 3 | EnergyPro load sizing calcs
MF | Davis, CA | 30-40% beyond 2008 | 1000 | 14280 | 31389 | Heat Pump | 19700 | 24625 | 24.625 | 3 | EnergyPro load sizing calcs
MF | Davis, CA | 30-40% beyond 2008 | 1282 | 16005 | 35961 | Heat Pump | 19700 | 24625 | 19.2083 | 3 | EnergyPro load sizing calcs
MF | Davis, CA | 30-40% beyond 2008 | 1282 | 17252 | 32355 | Heat Pump | 19700 | 24625 | 19.2083 | 3 | EnergyPro load sizing calcs
MF | Davis, CA | 30-40% beyond 2008 | 792 | 11650 | 19841 | Heat Pump | 14000 | 17500 | 22.096 | 2 | EnergyPro load sizing calcs
MF | Davis, CA | 30-40% beyond 2008 | 792 | 11650 | 19819 | Heat Pump | 14000 | 17500 | 22.096 | 2 | EnergyPro load sizing calcs
MF | Davis, CA | 30-40% beyond 2008 | 1282 | 17252 | 31574 | Heat Pump | 19700 | 24625 | 19.2083 | 3 | EnergyPro load sizing calcs
MF | Davis, CA | 30-40% beyond 2008 | 1282 | 14684 | 33725 | Heat Pump | 19700 | 24625 | 19.2083 | 3 | EnergyPro load sizing calcs
MF | Davis, CA | 30-40% beyond 2008 | 792 | 10159 | 20248 | Heat Pump | 14000 | 17500 | 22.096 | 2 | EnergyPro load sizing calcs
MF | Davis, CA | 30-40% beyond 2008 | 792 | 10159 | 20225 | Heat Pump | 14000 | 17500 | 22.096 | 2 | EnergyPro load sizing calcs
MF | Davis, CA | 30-40% beyond 2008 | 1282 | 14684 | 32824 | Heat Pump | 19700 | 24625 | 19.2083 | 3 | EnergyPro load sizing calcs
MF | Davis, CA | 30-40% beyond 2008 | 1282 | 15636 | 35049 | Heat Pump | 19700 | 24625 | 19.2083 | 3 | EnergyPro load sizing calcs
MF | Davis, CA | 30-40% beyond 2008 | 792 | 10747 | 20525 | Heat Pump | 14000 | 17500 | 22.096 | 2 | EnergyPro load sizing calcs
MF | Davis, CA | 30-40% beyond 2008 | 792 | 10747 | 20515 | Heat Pump | 14000 | 17500 | 22.096 | 2 | EnergyPro load sizing calcs
MF | Davis, CA | 30-40% beyond 2008 | 1282 | 14684 | 32824 | Heat Pump | 19700 | 24625 | 19.2083 | 3 | EnergyPro load sizing calcs
[8 empty] | BTUh Input 80 AFUE per sq ft | 25.3254
[8 empty] | Standard Dev | 7.3645
[7 empty] | House | 2750 | 69644.9624
SF | Danville, CA | [9 empty] | Radiant system, 50pg Man J report
No installed equip info
Radiant system w/ multiple zones, doesn't look like we have equip info.
No installed equip info
No installed equip info
Can't find project folder
No installed equip info
Can't find project folder
No installed equip info